# PRODUCT SPECIFICATION GUIDE

## MODEL: EXTRUDED ALUMINUM SCREENS

# DIVISION 10 – SPECIALTIES 
(PREVIOUSLY DIVISION 10 & 15)

***************************************************************************************************************

Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) Format.

The section must be carefully reviewed and edited by the Engineer to meet the requirements of the project and local building code.  Coordinate with other specification sections and the drawings.

Delete all "Specifier Notes" when editing this section.

## ***************************************************************************************************************

SECTION 108200

GRILLES AND SCREENS

- GENERAL

      - SECTION INCLUDES

        - Extruded Aluminum Screens with Horizontal Inverted J- Blades.

      - RELATED SECTIONS

        - Section 033000 – Cast-in-Place Concrete

        - Section 042000 – Unit Masonry.

        - Section 051000 – Structural Metal Framing.

        - Section 061000 – Rough Carpentry.

        - Section 074200 – Metal Wall Panels.

        - Section 076000 – Flashing and Sheet Metal.

        - Section 079000 – Joint Protection.

        - Section 089500 – Vents.

        - Section 099113 – Exterior Painting.

      - REFERENCES

        - AAMA 2604 – High Performance Organic Coatings on Aluminum Extrusions and Panels.

        - AAMA 2605 – Superior Performance Organic Coatings on Aluminum Extrusions and Panels.

        - ASCE 7 – Minimum Design Loads for Buildings and Other Structures.

        - ASTM B209 – Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate.

        - ASTM B221 – Standard Specifications for Aluminum and Aluminum-Alloy Extruded Bars, Rods, Wires, Profiles, and Tubes.

        - ASTM D822 – Standard Practice for Filtered Open-Flame Carbon-Arc Exposure of Paint and Related Coatings.

        - ASTM D4214 – Standard Test Method for Evaluating the Degree of Chalking of Exterior Paint Films.

        - ASTM D2244 – Standard Test Method for Calculation of Color Differences from Instrumentally Measured Color Coordinates.

        - ASTM E 90 – Laboratory Measurements of Airborne Sound Transmission Loss of Building Partitions.

      - SUBMITTALS

        - Comply with requirements of Section 013300 - Submittal Procedures.

        - Product Data:  Submit manufacturer's product data.

          - Printed catalog pages showing specified model and ratings.

        - Shop Drawings: Submit shop drawings indicating materials, construction,   dimensions, accessories, and installation details.

        - Samples:  Submit color chip sample for units with factory-applied paint.

      - QUALITY ASSURANCE

        - Sight screens shall be warranted against manufacturing defects for a period of 5 years.

      - DELIVERY, STORAGE, AND HANDLING

        - Delivery:  Deliver materials to site in manufacturer's original, unopened containers and packaging, with labels clearly indicating manufacturer, material, and location of installation.

        - Storage:  Store materials in a dry area indoor and protected from damage and in accordance with manufacturer’s instructions.

        - Handling: Protect materials and finishes during handling and installation to prevent damage.

        - Store and dispose of solvent-based materials, and material used with solvent based materials, in accordance with requirements of local authorities having jurisdiction.

      - PROJECT CONDITIONS

        - Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by the manufacturer for optimum results.  Do not install products under environmental conditions outside manufacturer’s absolute limits.

        - Field Measurements:  Verify actual dimensions of openings by field measurements before fabrication.

- PRODUCTS

      - MANUFACTURER

        - All-Lite, 5101 Blue Mound Road, Fort Worth, TX 76106.  Phone (817) 509-2300, www.alllite-louvers.com.

      - EXTRUDED ALUMINUM SIGHT SCREEN

        - Model:  HJ-445.

        - Construction:

          - Material: Mill finish 6063-T5 extruded aluminum.

          - Frame:  2” x 1-1/2” x 0.081” thick (51 x 38 x 2) angle.

          - Blades:  45° X 0.081” (2) thick J-style.

          - Mullion:  Visible.

        - Performance Data:

          - Based on testing 48 inch x 48 inch (1222 x 1222) size unit in accordance with AMCA 500L.

          - Free Area: 50.0% nominal

          - Free area size: 8.0 ft² (0.74m²)

        - Design Load:

          - Wind Load:  Sight screen designs shall withstand the effects of 30 psf (1.44 kPa) of uniform pressure acting inward or outward.

          - Seismic Performance:  Sight screens, including attachments to other construction, shall withstand seismic effects determined by ASCE-7.

      - FINISHES

        - Finish sight screens after assembly as follows:

***************************************************************************************************************

Specifier Notes:  Select one of the following.

***************************************************************************************************************

- Mill finish

- High Performance Fluoropolymer:  Complying with AAMA 2605 and containing not less than 100 percent PVDF resin by weight in color coat Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers’ written instructions.

  - Color and Gloss:  [As indicated by manufacturer’s designations]  [Match Architect’s sample]  [As selected by Architect from manufacturer’s full range]  <Insert color and gloss>

- Clear Anodize:  Complying with AA-C22A41, Class-1, 0.7 mils (0.018mm) minimum thickness.

      - Color:  Clear 215-R1

- Integral Color Anodize:  Complying with AA-C22A44, Class-1, 0.7 mils (0.018mm) minimum thickness

      - Color:  [Champagne]  [Light Bronze]  [Medium Bronze]  [Dark Bronze]  [Black]

- EXECUTION

      - EXAMINATION

        - Examine substrates and openings for compliance with requirements for installation tolerances and other conditions affecting performance.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - PREPARATION

        - Clean opening thoroughly prior to installation.

        - Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.

      - INSTALLATION

        - Install sight screens at locations as indicated on the drawings and in accordance with manufacturer’s instructions.

        - Install sight screens plumb, level, in plane of wall, and in alignment with adjacent work.

      - ADJUSTING AND CLEANING

        - Clean exposed surfaces of sight screens with water and mild soap or detergent not harmful to finish taking care to remove fingerprints and soil.  Thoroughly rinse surfaces and dry.  Do not let soil accumulate during construction period.

        - Touch-up, repair, or replace sight screens damaged during installation and construction so that no evidence remains of the corrective work.

END OF SECTION